## Hydrogen
Hydrogen Storage | [7 empty] | Total Load (MWh): | 437087.07
No Restrictions | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min? |  |  | Renewables with CSP & Hydrogen Storage
Wind | 116276 |  | 91 | 10581116 | 306442 | 38.44% | none |  |  | Scenarios | No Restrictions | Limited Wind (<25 MW) | No CSP
PV | 75772 |  | 104 | 7880288 | 88546 | 9.719% | none |  |  | LCOE ($/MWh) | 116.2341 | 121.9437 | 123.5434
CSP | 291720 |  | 0 | 0 | 0 | #DIV/0! | min |  |  | Land Use (km^2) | 5.2739 | 6.53 | 6.9857
Diesel | 154460 | 170 | 35 | 5406100 | 50888 | 16.6% | none |  |  | Solar PV (MW) | 301 | 378 | 411
[10 empty] | Wind (MW) | 54 | 25 | 32
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min? |  |  | CSP (MW) | 6 | 4 | N/A
Utility | 15700 | 0 | 170 | 2669000 | 2.4286 |  | none |  |  | Utility Storage (MWh)/Hours of Storage | 420/6 | 420/6 | 420/6
Thermal | 4290 | 0 | 0 | 0 | 0 |  | min |  |  | CSP Thermal Storage (MWh)/Hours of Storage | 1014/14.5 | 823/11.75 | N/A
Hydrogen Storage | 2860 | 2 | 248 | 709280 | 35.4286 |  | none |  |  | Hydrogen Storage (MWh)/Hours of Storage | 2000 | 1782 | 2000
[10 empty] | Hydrogen Electrolyzer (MW) | 29 | 51 | 58
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min? |  |  | Hydrogen Fuel Cell (MW) | 19 | 23 | 43
Hydrogen Electrolyzer | 85810 |  | 3 | 257430 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 7 | 300370 |  |  | none
|  |  | Capital Cost: | 36454544 | LCOE ($/MWh): |  | 83.4034
[5 empty] | Land Use (km^2): |  | 1.7677
No Diesel
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 54 | 6278904 | 199924 | 42.26% | none
PV | 75772 |  | 301 | 22807372 | 259265 | 9.833% | none
CSP | 291720 |  | 6 | 1750320 | 8965 | 17.06% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 43 | 420 | 6594000 | 6 |  | max
Thermal | 4290 | 73 | 1014 | 4350060 | 14.4857 |  | none
Hydrogen Storage | 2860 | 0 | 2000 | 5720000 | 105.2632 |  | max
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min?
Hydrogen Electrolyzer | 85810 |  | 29 | 2488490 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 19 | 815290 |  |  | none
|  |  | Capital Cost: | 50804436 | LCOE ($/MWh): |  | 116.2341
[5 empty] | Land Use (km^2): |  | 5.2739
Limited Wind (<25)
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 25 | 2906900 | 89090 | 40.68% | max
PV | 75772 |  | 378 | 28641816 | 400518 | 12.1% | none
CSP | 291720 |  | 4 | 1166880 | 6540 | 18.66% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 129 | 420 | 6594000 | 6 |  | max
Thermal | 4290 | 77 | 823 | 3530670 | 11.7571 |  | none
Hydrogen Storage | 2860 | 58 | 1782 | 5096520 | 77.4783 |  | none
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min?
Hydrogen Electrolyzer | 85810 |  | 51 | 4376310 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 23 | 986930 |  |  | none
|  |  | Capital Cost: | 53300026 | LCOE ($/MWh): |  | 121.9437
[5 empty] | Land Use (km^2): |  | 6.53
No Batteries
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 25 | 2906900 | 84766 | 38.71% | none
PV | 75772 |  | 490 | 37128280 | 534537 | 12.45% | max
CSP | 291720 |  | 10 | 2917200 | 16408 | 18.73% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Thermal | 4290 | 107 | 1087 | 4663230 | 15.5286 |  | none
Hydrogen Storage | 2860 | 251 | 2000 | 5720000 | 27.027 |  | max
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min?
Hydrogen Electrolyzer | 85810 |  | 175 | 15016750 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 74 | 3175340 |  |  | none
|  |  | Capital Cost: | 71527700 | LCOE ($/MWh): |  | 163.6463
[5 empty] | Land Use (km^2): |  | 8.5915
No CSP
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 32 | 3720832 | 117086 | 41.77% | none
PV | 75772 |  | 411 | 31142292 | 370898 | 10.3% | max
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 132 | 420 | 6594000 | 6 |  | max
Hydrogen Storage | 2860 | 0 | 2000 | 5720000 | 46.5116 |  | max
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min?
Hydrogen Electrolyzer | 85810 |  | 58 | 4976980 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 43 | 1845130 |  |  | none
|  |  | Capital Cost: | 53999234 | LCOE ($/MWh): |  | 123.5434
[5 empty] | Land Use (km^2): |  | 6.9857
Bigger Batteries
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 50 | 5813800 | 185968 | 42.46% | none
PV | 75772 |  | 312 | 23640864 | 276834 | 10.13% | none
CSP | 291720 |  | 5 | 1458600 | 7766 | 17.73% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 59 | 488 | 7661600 | 6.9714 |  | max
Thermal | 4290 | 316 | 893 | 3830970 | 12.7571 |  | none
Hydrogen Storage | 2860 | 16 | 1806 | 5165160 | 112.875 |  | none
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min?
Hydrogen Electrolyzer | 85810 |  | 30 | 2574300 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 16 | 686560 |  |  | none
|  |  | Capital Cost: | 50831854 | LCOE ($/MWh): |  | 116.2969
[5 empty] | Land Use (km^2): |  | 5.4345
Increased Solar
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 63 | 7325388 | 234770 | 42.54% | none
PV | 102973 |  | 273 | 28111629 | 215957 | 9.03% | none
CSP | 291720 |  | 8 | 2333760 | 11654 | 16.63% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 6 | 420 | 6594000 | 6 |  | max
Thermal | 4290 | 77 | 1272 | 5456880 | 18.1714 |  | none
Hydrogen Storage | 2860 | 0 | 2000 | 5720000 | 117.6471 |  | max
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min?
Hydrogen Electrolyzer | 85800 |  | 24 | 2059200 |  |  | none
Hydrogen Fuel Cell | 42900 |  | 17 | 729300 |  |  | none
|  |  | Capital Cost: | 58330157 | LCOE ($/MWh): |  | 133.452
[5 empty] | Land Use (km^2): |  | 4.8506

## Anitgua Current System
Antigua Current Energy System | [7 empty] | 2020 load | 349669.656
[8 empty] | 2035 load | 437087.07
Current System | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generated | Capacity Factor | Max/min? |  |  | Presentable Results | Antigua Current and Future Business as Usual System
Diesel | 154460 | 170 | 53.37 | 65283630.2 | 335530 | 71.77% | none |  |  |  | Scenarios | Current System | 2035 System
Solar PV | 75772 |  | 9 | 681948 | 14139 | 17.93% | none |  |  |  | LCOE ($/MWh) | 188.6511 | 189.6388
[11 empty] | Diesel (MW) | 53.5 | 66.75
|  |  | Capital Cost: | 65965578.2 | LCOE ($/MWh): |  | 188.6511 |  |  |  | Solar PV (MW) | 9 | 9
Diesel System in 2035 | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generated | Capacity Factor | Max/min?
Diesel | 154460 | 170 | 66.72 | 82206731.2 | 422948 | 72.36% | none
Solar PV | 75772 |  | 9 | 681948 | 14139 | 17.93% | none
|  |  | Capital Cost: | 82888679.2 | LCOE ($/MWh): |  | 189.6388

## Only Wind,PV,Batteries
No CSP | [7 empty] | Total Load (MWh): | 437087.07
25MW Wind | Inputs |  | Results | [6 empty] | Presentable Results | Solar PV, Wind, and Batteries Only
Generators | Capital Cost ($/MW) |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min? |  |  |  | Scenarios | 25 MW Wind Max | 50 MW Wind Max | 100 MW Wind Max
Wind | 116276 |  | 25 | 2906900 | 90937 | 41.52% | max |  |  |  | LCOE ($/MWh) | 169.0919 | 155.4767 | 154.191
PV | 75772 |  | 608 | 46069376 | 365188 | 6.857% | none |  |  |  | Land Use (km^2) | 10.3341 | 7.6146 | 7.1387
[11 empty] | Solar PV (MW) | 608 | 448 | 420
Batteries | Capital Cost ($/kWh) | e_initial | MWh | Cost ($) |  | Hours of Storage | Max/min? |  |  |  | Wind (MW) | 25 | 50 | 73
Utility | 15700 | 403 | 1588 | 24931600 |  | 26.4667 | none |  |  |  | Utility Storage (MWh) | 1588 | 1796 | 1725
|  |  | Capital Cost: | 73907876 |  | LCOE ($/MWh): | 169.0919 |  |  |  | Hours of Storage (Hours) | 26.4667 | 29.9333 | 28.75
50MW Wind | [5 empty] | Land Use (km^2): | 10.3341
Generators | Capital Cost ($/MW) |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 50 | 5813800 | 186722 | 42.63% | max
PV | 75772 |  | 448 | 33945856 | 264130 | 6.73% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh | Cost ($) |  | Hours of Storage | Max/min?
Utility | 15700 | 58 | 1796 | 28197200 |  | 29.9333 | none
|  |  | Capital Cost: | 67956856 |  | LCOE ($/MWh): | 155.4767
100MW Wind | [5 empty] | Land Use (km^2): | 7.6146
Generators | Capital Cost ($/MW) |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 73 | 8488148 | 268613 | 42% | none
PV | 75772 |  | 420 | 31824240 | 178193 | 4.843% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh | Cost ($) |  | Hours of Storage | Max/min?
Utility | 15700 | 0 | 1725 | 27082500 |  | 28.75 | none
|  |  | Capital Cost: | 67394888 |  | LCOE ($/MWh): | 154.191
[6 empty] | Land Use (km^2): | 7.1387

## CSP
CSP | [7 empty] | Total Load (MWh): | 437087.07
25MW Wind | Inputs |  | Results
Generators | Capital Cost |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 25 | 2906900 | 91360 | 41.72% | max |  |  | Presentable Results | Renewables with CSP
PV | 75772 |  | 402 | 30460344 | 327859 | 9.31% | none |  |  |  | Scenarios | 25 MW Wind Max | 50 MW Wind Max | 100 MW Wind Max
CSP | 291720 |  | 22 | 6417840 | 33822 | 17.55% | none |  |  |  | LCOE ($/MWh) | 127.6633 | 119.0002 | 118.0308
[11 empty] | Land Use (km^2) | 7.4114 | 6.1334 | 5.8999
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  |  | Hours of Storage | Max/min? |  |  |  | Solar PV (MW) | 402 | 333 | 327
Utility | 15700 | 164 | 561 | 8807700 |  | 8.0143 | none |  |  |  | Wind (MW) | 25 | 50 | 62
Thermal | 4290 | 1191 | 1680 | 7207200 |  | 24 | none |  |  |  | CSP (MW) | 22 | 18 | 13
|  |  | Capital Cost: | 55799984 |  | LCOE ($/MWh): | 127.6633 |  |  |  | Utility Storage (MWh)/Hours of Storage | 561/8 | 542/7.75 | 548/7.8
50MW Wind | [5 empty] | Land Use (km^2): | 7.4114 |  |  |  | CSP Thermal Storage (MWh)/Hours of Storage | 1680/24 | 1680/24 | 1680/24
Generators | Capital Cost ($/MW) |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 50 | 5813800 | 184236 | 42.06% | max
PV | 75772 |  | 333 | 25232076 | 236869 | 8.12% | none
CSP | 291720 |  | 18 | 5250960 | 27354 | 17.35% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh | Cost ($) |  | Hours of Storage | Max/min?
Utility | 15700 | 58 | 542 | 8509400 |  | 7.7429 | none
Thermal | 4290 | 873 | 1680 | 7207200 |  | 24 | max
|  |  | Capital Cost: | 52013436 |  | LCOE ($/MWh): | 119.0002
100MW Wind | [5 empty] | Land Use (km^2): | 6.1334
Generators | Capital Cost ($/MW) |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 62 | 7209112 | 230765 | 42.49% | none
PV | 75772 |  | 327 | 24777444 | 197298 | 6.888% | none
CSP | 291720 |  | 13 | 3792360 | 18657 | 16.38% | none
Batteries | Capital Cost ($/MWh) | e_initial | MWh | Cost ($) |  | Hours of Storage | Max/min?
Utility | 15700 | 9 | 548 | 8603600 |  | 7.8286 | none
Thermal | 4290 | 0 | 1680 | 7207200 |  | 24 | max
|  |  | Capital Cost: | 51589716 |  | LCOE ($/MWh): | 118.0308
[6 empty] | Land Use (km^2): | 5.8999
Increased Solar Cost | Inputs |  | Results
Generators | Capital Cost |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 25 | 2906900 | 93507 | 42.7% | max
PV | 102973 |  | 372 | 38305956 | 305213 | 9.366% | none
CSP | 291720 |  | 33 | 9626760 | 52471 | 18.15% | none
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  |  | Hours of Storage | Max/min?
Utility | 15700 | 114 | 538 | 8446600 |  | 7.6857 | none
Thermal | 4290 | 792 | 1680 | 7207200 |  | 24 | none
|  |  | Capital Cost: | 66493416 |  | LCOE ($/MWh): | 152.1285
[6 empty] | Land Use (km^2): | 7.1909
Decreased Solar Cost; 25MW Wind | Inputs |  | Results
Generators | Capital Cost |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 25 | 2906900 | 93549 | 42.72% | max
PV | 47196 |  | 432 | 20388672 | 332141 | 8.777% | none
CSP | 291720 |  | 18 | 5250960 | 27798 | 17.63% | none
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  |  | Hours of Storage | Max/min?
Utility | 15700 | 123 | 555 | 8713500 |  | 7.9286 | none
Thermal | 4290 | 703 | 1631 | 6996990 |  | 23.3 | none
|  |  | Capital Cost: | 44257022 |  | LCOE ($/MWh): | 101.2545
[6 empty] | Land Use (km^2): | 7.8161
Increased CSP Cost; 25MW Wind | Inputs |  | Results
Generators | Capital Cost |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min? | Sensitivity Tests Continued
Wind | 116276 |  | 25 | 2906900 | 91360 | 41.72% | max | Scenarios | CSP CAPEX Increased | CSP CAPEX Decreased
PV | 75772 |  | 402 | 30460344 | 327859 | 9.31% | none | LCOE ($/MWh) | 133.9397 | 121.1624
CSP | 350107 |  | 22 | 7702354 | 33822 | 17.55% | none | Land Use (km^2) | 7.4114 | 7.2479
[8 empty] | Solar PV (MW) | 402 | 380
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  |  | Hours of Storage | Max/min? | Wind (MW) | 25 | 25
Utility | 15700 | 121 | 562 | 8823400 |  | 8.0286 | none | CSP (MW) | 22 | 30
Thermal | 5149 | 676 | 1680 | 8650320 |  | 24 | none | Utility Storage (MWh)/Hours of Storage | 562/8 | 541/7.75
|  |  | Capital Cost: | 58543318 |  | LCOE ($/MWh): | 133.9397 | CSP Thermal Storage (MWh)/Hours of Storage | 1680/24 | 1680/24
[6 empty] | Land Use (km^2): | 7.4114
Decreased CSP Cost; 25MW Wind | Inputs |  | Results
Generators | Capital Cost |  | MW | Cost ($) | Power Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 25 | 2906900 | 91360 | 41.72% | max
PV | 75772 |  | 380 | 28793360 | 310683 | 9.333% | none
CSP | 233405 |  | 30 | 7002150 | 47524 | 18.08% | none
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  |  | Hours of Storage | Max/min?
Utility | 15700 | 116 | 541 | 8493700 |  | 7.7286 | none
Thermal | 3430 | 865 | 1680 | 5762400 |  | 24 | none
|  |  | Capital Cost: | 52958510 |  | LCOE ($/MWh): | 121.1624
[6 empty] | Land Use (km^2): | 7.2479

## Small Diesel
Small Diesel with limited batteries | [7 empty] | Total Load (MWh): | 437087.07
No Restrictions | Inputs |  | Results | [9 empty] | Presentable Results | Small Diesel Contribution
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min? | [6 empty] | Scenarios | No Restrictions | 10 MW Diesel | 5 MW Diesel | 3 MW Diesel
Wind | 116276 |  | 91 | 10581116 | 298942 | 37.5% | none | [6 empty] | LCOE ($/MWh) | 83.3335 | 99.3871 | 110.1648 | 116.7427
PV | 75772 |  | 103 | 7804516 | 87951 | 9.748% | none | [6 empty] | Land Use (km^2) | 1.7562 | 4.35 | 5.1707 | 5.6745
CSP | 291720 |  | 0.21 | 61261.2 | 335 | 18.21% | none | [6 empty] | Solar PV (MW) | 103 | 242 | 281 | 306
Diesel | 154460 | 170 | 37.5 | 14892350 | 53530 | 16.3% | none | [6 empty] | Wind (MW) | 91 | 53 | 62 | 69
[14 empty] | CSP (MW) | 0.21 | 9 | 15 | 18
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min? | [6 empty] | Diesel (MW) | 37.5 | 10 | 5 | 3
Utility | 15700 | 0 | 182 | 2857400 | 2.6 |  | none | [6 empty] | Utility Storage (MWh)/Hours of Storage | 182/2 | 420/6 | 420/6 | 420/6
Thermal | 4290 | 0 | 53 | 227370 | 0.75714 |  | none | [6 empty] | CSP Thermal Storage (MWh)/Hours of Storage | 53/0.75 | 1397/20 | 1680/24 | 1680/24
|  |  | Capital Cost: | 36424013.2 |  | LCOE ($/MWh): | 83.3335 | [6 empty] | Renewable Energy Penetration (%) | 88 | 97 | 99 | 99.6
[5 empty] | 87.75% | Land Use (km^2): | 1.7562
^Renewable Penetration^
10 MW Diesel | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 53 | 6162628 | 197572 | 42.55% | none
PV | 75772 |  | 242 | 18336824 | 223207 | 10.53% | none
CSP | 291720 |  | 9 | 2625480 | 14152 | 17.95% | none
Diesel | 154460 | 170 | 10 | 3728760 | 12848 | 14.67% | max
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 27 | 420 | 6594000 | 6 |  | max
Thermal | 4290 | 0 | 1397 | 5993130 | 19.9571 |  | none
|  |  | Capital Cost: | 43440822 |  | LCOE ($/MWh): | 99.3871
[5 empty] | 97.06% | Land Use (km^2): | 4.35
^Renewable Penetration^
5 MW Diesel | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 62 | 7209112 | 226886 | 41.77% | none
PV | 75772 |  | 281 | 21291932 | 190817 | 7.752% | none
CSP | 291720 |  | 15 | 4375800 | 23826 | 18.13% | none
Diesel | 154460 | 170 | 5 | 1473550 | 4125 | 9.418% | max
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 11 | 420 | 6594000 | 6 |  | max
Thermal | 4290 | 351 | 1680 | 7207200 | 24 |  | max
|  |  | Capital Cost: | 48151594 |  | LCOE ($/MWh): | 110.1648
[5 empty] | 99.06% | Land Use (km^2): | 5.1707
^Renewable Penetration^
3 MW Diesel | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MWh | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 69 | 8023044 | 248211 | 41.06% | none
PV | 75772 |  | 306 | 23186232 | 165430 | 6.171% | none
CSP | 291720 |  | 18 | 5250960 | 28770 | 18.25% | none
Diesel | 154460 | 170 | 3 | 765300 | 1776 | 6.758% | max
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 0 | 420 | 6594000 | 6 |  | max
Thermal | 4290 | 1 | 1680 | 7207200 | 24 |  | max
|  |  | Capital Cost: | 51026736 |  | LCOE ($/MWh): | 116.7427
[5 empty] | 99.59% | Land Use (km^2): | 5.6745
^Renewable Penetration^
86% Renewable Penetration - Any | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MWh | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min? | [6 empty] | Constant 7 MW Diesel Contribution
Wind | 116276 |  | 36 | 4185936 | 248211 | 78.71% | none | [6 empty] | Scenarios | No Restrictions | No Hydrogen | No Hydrogen or CSP
PV | 75772 |  | 274 | 20761528 | 165430 | 6.892% | none | [6 empty] | LCOE ($/MWh) | 122.0195 | 123.6149 | 146.8164
CSP | 291720 |  | 3.5 | 1021020 | 28770 | 93.84% | none | [6 empty] | Land Use (km^2) | 4.7492 | 5.0013 | 6.4418
Diesel | 154460 | 170 | 7 | 11505620 | 61320 | 100% | max | [6 empty] | Solar PV (MW) | 274 | 278 | 379
[14 empty] | Wind (MW) | 36 | 43 | 28
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  | Hours of Storage |  | Max/min? | [6 empty] | CSP (MW) | 3.5 | 10.5 | N/A
Utility | 15700 | 61 | 473 | 7426100 | 6.7571 |  | max | [6 empty] | Utility Storage (MWh)/Hours of Storage | 473/6.8 | 488/7 | 1318/18.8
Thermal | 4290 | 0 | 463 | 1986270 | 6.6143 |  | max | [6 empty] | CSP Thermal Storage (MWh)/Hours of Storage | 463/6.6 | 1337/19.1 | N/A
Hydrogen Storage | 2860 | 39 | 1804 | 5159440 | 128.8571 |  | max | [6 empty] | Hydrogen Storage (MWh)/Hours of Storage | 1804/129 | N/A | N/A
[14 empty] | Hydrogen Electrolyzer (MW) | 8 | N/A | N/A
Links | Capital Cost ($/MW) |  | MW |  |  |  | Max/min? | [6 empty] | Hydrogen Fuel Cell (MW) | 14 | N/A | N/A
Hydrogen Electrolyzer | 85810 |  | 8 | 686480 |  |  | none
Hydrogen Fuel Cell | 42910 |  | 14 | 600740 |  |  | none
|  |  | Capital Cost: | 53333134 |  | LCOE ($/MWh): | 122.0195
[5 empty] | 85.97% | Land Use (km^2): | 4.7492
^Renewable Penetration^
86% Renewable Penetration - No Hydrogen | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MWh | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 43 | 4999868 | 248211 | 65.89% | none
PV | 75772 |  | 278 | 21064616 | 165430 | 6.793% | none
CSP | 291720 |  | 10.5 | 3063060 | 28770 | 31.28% | none
Diesel | 154460 | 170 | 7 | 11505620 | 61320 | 100% | max
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 61 | 488 | 7661600 | 6.9714 |  | max
Thermal | 4290 | 0 | 1337 | 5735730 | 19.1 |  | max
|  |  | Capital Cost: | 54030494 |  | LCOE ($/MWh): | 123.6149
[5 empty] | 85.97% | Land Use (km^2): | 5.0013
^Renewable Penetration^
86% Renewable Penetration - No Hydrogen or CSP | Inputs |  | Results
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MWh | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min?
Wind | 116276 |  | 28 | 3255728 | 105062 | 42.83% | none
PV | 75772 |  | 379 | 28717588 | 285542 | 8.601% | none
Diesel | 154460 | 170 | 7 | 11505620 | 61320 | 100% | max
Batteries | Capital Cost ($/kWh) | e_initial | MWh |  | Hours of Storage |  | Max/min?
Utility | 15700 | 907 | 1318 | 20692600 | 18.8286 |  | max
|  |  | Capital Cost: | 64171536 |  | LCOE ($/MWh): | 146.8164
[5 empty] | 85.97% | Land Use (km^2): | 6.4418
^Renewable Penetration^
MC - Marginal Cost
No Restrictions - Higher Diesel MC | Inputs |  | Results | [5 empty] | Sensitivity Tests
Generators | Capital Cost ($/MW) | Marginal Cost ($/MWh) | MW | Cost ($) | Energy Generation (MWh) | Capacity Factor | Max/min? |  | Scenarios | No Restrictions | Solar PV CAPEX Increased | Solar PV CAPEX Decreased
Wind | 116276 |  | 118 | 13720568 | 329819 | 31.91% | none |  | LCOE ($/MWh) | 128.4258 | 152.1285 | 101.2545
PV | 75772 |  | 316 | 23943952 | 99095 | 3.58% | none |  | Land Use (km^2) | 5.7919 | 7.1909 | 7.8161
CSP | 291720 |  | 16 | 4667520 | 13911 | 9.925% | none |  | Solar PV (MW) | 316 | 372 | 432
Diesel | 154460 | 240 | 0 | 0 | 0 | #DIV/0! | none |  | Wind (MW) | 118 | 25 | 25
[9 empty] | CSP (MW) | 16 | 33 | 18
Batteries | Capital Cost ($/MWh) | e_initial | MWh |  | Hours of Storage |  | Max/min? |  | Diesel (MW) | 0 | N/A | N/A
Utility | 15700 | 0 | 420 | 6594000 | 6 |  | none |  | Utility Storage (MWh)/Hours of Storage | 420/6 | 420/6 | 555/7.9
Thermal | 4290 | 0 | 1680 | 7207200 | 24 |  | none |  | CSP Thermal Storage (MWh)/Hours of Storage | 1680/24 | 1680/24 | 1631/23.3
|  |  | Capital Cost: | 56133240 |  | LCOE ($/MWh): | 128.4258
[5 empty] | 100% | Land Use (km^2): | 5.7919
^Renewable Penetration^

## Available Land_Plant Land Use
Available Industrial Land in Antigua
Sites | Area (acres) | Area (m^2)
West Indies Oil Company | 135.6837 | 549092.89
Crabbs Peninsula | 441.5769 | 1787000
Land Use By Renewable Source
Renewable Source | Area Use (acre/MW) | Land Use (m^2/MW) | 30,000 houses with solar (4 kW per house)
Solar PV | 4.2 | 16996.812 | 2.0396 | km^2
CSP | 6.5 | 26304.59
Wind | ??
| 1 | 4046.86